## DAR Old (hidden)
| Project No. | Date
| Sheet No. | Computed by
Subject | Checked by | Approved by
DESIGN CALCULATION
SHEET
of

## DAR (hidden)
Design calculation sheet
Project no.: | Date: | Sheet no.: | 25 | 25 | Computed by:
Subject |  |  |  |  | Checked by:
Approved by:
of

## G001
Design calculation sheet
Project no: | S08050 |  | Date: | 15/10/09 | Sheet no.: | 1 | 4 | Computed by: |  | B.S.K
Subject: | Foam Fire Extinguishing System Calculations | [6 empty] | Checked by: |  | B.H
| jeddah site- fuel tanks | [6 empty] | Approved by: |  | T.Q
General Assumptions:
1- The calculation presented here below are for reference and guidance only,
as foam system is a pre-engineered system to come complete from the supplier.
2- The system used is an automatic sprinkler systems utilizing
foam/water sprinkler heads, integrated into a complete deluge system.
1- Electrical Sub-station No. 39.2:
1.1- Generator Room No. (G001):
Design Criteria and Preliminary Estimation:
| Discharge Criteria = |  |  | 6.5 | l/min.m2 = | 0.16 | gpm/ft2 | (Refer to NFPA 16, section 4-3.2)
| Discharge Duration = |  |  | 10 | min. | (Refer to NFPA 16, section 4-3.3.1)
| Foam Concentrate = |  |  | 3 | % | (Refer to Wilson fire equipment,
warehouse foam fire protection systems
design bulliten attached)
| Room Area = |  | 207.3 | m2
| Min. Area per Sprinkler = |  |  | 9 | m2 | (Refer to NFPA 16, section 4-3.7.2)
| Min. No. of sprinklers = |  |  | 23.0333 | = | 24 | Sprinklers
But for the maximum spacing between sprinklers not to exceed 3.7 m
(Refer to NFPA 16, section 4-3.7.2)
| Actual No. of sprinklers = |  |  | 25 | Sprinklers |  | (Refer to attached drawings)
Design calculation sheet
Project no: | S08050 |  | Date: | 15/10/09 | Sheet no.: | 2 | 4 | Computed by: |  | B.S.K
Subject: | Foam Fire Extinguishing System Calculations | [6 empty] | Checked by: |  | B.H
| jeddah site- fuel tanks | [6 empty] | Approved by: |  | T.Q
And hence,
Flow of foam solution = Discharge Criteria x Room Area
(Refer to NFPA 16, section 4-3.3.1)
| Flow of foam solution = |  |  | 1348 | l/min.
Volume of foam solution = Flow Of Foam Solution x Discharge Duration
| Volume of foam solution = |  |  | 13480 | l
Quantity of Foam Concentrate = Volume Of Foam Solution x Foam Concentration
| Quantity of foam Conc. = |  |  | 404.4 | l = | 106.8312 | Gallons
| Foam Tank Capacity = |  |  | 107 | Gallons
| Design Pressure at Nozzle = |  |  |  | 207.6 | kPa | = | 30.102 | psi
| Hydraulic Calculations: |  |  |  | (Refer to NFPA 16, section 4-4.1.3)
| Nozzle minimum operating pressure= |  |  |  | 30 | psi | (Refer to NFPA 15, section A.8.1.2)
(Refer to ANSUL foam systems
design and applications manual attached)
(Refer to Viking design data, attached)
| Type of foam concentrate used is AFFF |  |  |  |  | (Refer to NFPA 11, section 4.3.1.4)
| Density of foam concentrate (ρ) = |  |  |  | 1.011 | g/ml | (Refer to ANSUL design data, attached)
| Absolute Viscosity of foam concentrate (μ) = |  |  |  |  | 1.8 | cps
(Refer to Hypro design data, attached)
From the sprinkler distribution:
| Coverage area per sprinkler = |  |  |  | 8.31 | m2 = | 89.3548 | ft2
Design calculation sheet
Project no: | S08050 |  | Date: | 15/10/09 | Sheet no.: | 3 | 4 | Computed by: |  | B.S.K
Subject: | Foam Fire Extinguishing System Calculations | [6 empty] | Checked by: |  | B.H
| jeddah site- fuel tanks | [6 empty] | Approved by: |  | T.Q
Since,
For open type sprinklers dedicated for foam/water deluge systems,
Q (gpm) = K √P (psi)
And,
| K = | 3 | (Refer to ANSUL foam systems design and applications manual attached)
and since we have two approaches, one is to satisfy the density and the other is to satisfy
the minimum pressure required; we'll calculate both and apply the one with the greater demand.
i. Taking the design density as the governing constraint:
| Discharge Criteria = |  |  | 0.16 | gpm/ft2
| Q = | 14.2968 | gpm
| P = | 22.7109 | psi | (refused)
ii. Taking the minimum operating pressure as the governing constraint:
| P = | 30 | psi
| Q = | 16.4317 | gpm
| Discharge Criteria = |  |  | 0.18389 | gpm/ft2 | (accepted)
Therefore,
| Sp. No. | (gpm) | Pipe Diam.(in) | Eq. Pipe length (ft) |  | C | Pf (psi/ft) |  | Pt (psi)
| S1 | 16.4 | 0.5 | 8 |  | 120 | 3.3276 |  | 56.6208
| N1-N2 | 32.8 | 1 | 28 |  | 120 | 0.41022 |  | 68.107
| N2-N3 | 65.6 | 1.5 | 18 |  | 120 | 0.20529 |  | 71.8021
| N3-N4 | 98.4 | 2 | 9 |  | 120 | 0.10707 |  | 72.7658
| N4-System outlet | 98.4 | 2 | 15 |  | 120 | 0.10707 |  | 74.3719
Adding the static pressure:
|  |  |  | Pr = | 79 | psi
Design calculation sheet
Project no: | S08050 |  | Date: | 15/10/09 | Sheet no.: | 4 | 4 | Computed by: |  | B.S.K
Subject: | Foam Fire Extinguishing System Calculations | [6 empty] | Checked by: |  | B.H
| jeddah site- fuel tanks | [6 empty] | Approved by: |  | T.Q
Assuming that the induction causes a pressure drop of 30 % of the required pressure:
|  |  | Pt = | 103 | psi
Based on the final Design Criteria:
System Summary:
|  |  | Tank Capacity = |  | 123 | Gal.
|  |  | No. of Sprinklers = |  | 25 | Sprinklers
|  |  | Minimum Pressure Required at Input Point = |  |  |  |  | 103 | psi
of
of
of
of

## G001 (2)
Design calculation sheet
Project no: | K0065 |  | Date: | 21/4/03 | Sheet no.: | 1 | 4 | Computed by: |  | A.R
Subject: | Foam Fire Extinguishing System Calculations | [6 empty] | Checked by: |  | A.G
Approved by:
General Assumptions:
1- The calculation presented here below are for reference and guidance only,
as foam system is a pre-engineered system to come complete from the supplier.
2- The system used is an automatic sprinkler systems utilizing
foam/water sprinkler heads, integrated into a complete deluge system.
2- Electrical Sub-station No. 39A To E:
2.1- Generator Room No. (G001):
Design Criteria and Preliminary Estimation:
| Discharge Criteria = |  |  | 6.5 | l/min.m2 = | 0.16 | gpm/ft2 | (Refer to NFPA 16, section 4-3.2)
| Discharge Duration = |  |  | 10 | min. | (Refer to NFPA 16, section 4-3.3.1)
| Foam Concentrate = |  |  | 3 | % | (Refer to Wilson fire equipment,
warehouse foam fire protection systems
design bulliten attached)
| Room Area = |  | 38.7 | m2
| Min. Area per Sprinkler = |  |  | 9.3 | m2 | (Refer to NFPA 16, section 4-3.7.2)
| Min. No. of sprinklers = |  |  | 4.1613 | = | 5 | Sprinklers
But for the maximum spacing between sprinklers not to exceed 3.7 m
(Refer to NFPA 16, section 4-3.7.2)
| Actual No. of sprinklers = |  |  | 6 | Sprinklers |  | (Refer to attached drawings)
Design calculation sheet
Project no: | K0065 |  | Date: | 21/4/03 | Sheet no.: | 2 | 4 | Computed by: |  | A.R
Subject: | Foam Fire Extinguishing System Calculations | [6 empty] | Checked by: |  | A.G
Approved by:
And hence,
Flow of foam solution = Discharge Criteria x Room Area
(Refer to NFPA 16, section 4-3.3.1)
| Flow of foam solution = |  |  | 252 | l/min.
Volume of foam solution = Flow Of Foam Solution x Discharge Duration
| Volume of foam solution = |  |  | 2520 | l
Quantity of Foam Concentrate = Volume Of Foam Solution x Foam Concentration
| Quantity of foam Conc. = |  |  | 75.6 | l = | 19.9714 | Gallons
| Foam Tank Capacity = |  |  | 20 | Gallons
| Design Pressure at Nozzle = |  |  |  | 207.6 | kPa | = | 30.102 | psi
| Hydraulic Calculations: |  |  |  | (Refer to NFPA 16, section 4-4.1.3)
| Nozzle minimum operating pressure= |  |  |  | 30 | psi | (Refer to NFPA 15, section A.8.1.2)
(Refer to ANSUL foam systems
design and applications manual attached)
(Refer to Viking design data, attached)
| Type of foam concentrate used is AFFF |  |  |  |  | (Refer to NFPA 11, section 4.3.1.4)
| Density of foam concentrate (ρ) = |  |  |  | 1.011 | g/ml | (Refer to ANSUL design data, attached)
| Absolute Viscosity of foam concentrate (μ) = |  |  |  |  | 1.8 | cps
(Refer to Hypro design data, attached)
From the sprinkler distribution:
| Coverage area per sprinkler = |  |  |  | 6.3 | m2 = | 67.7419 | ft2
Design calculation sheet
Project no: | K0065 |  | Date: | 21/4/03 | Sheet no.: | 3 | 4 | Computed by: |  | A.R
Subject: | Foam Fire Extinguishing System Calculations | [6 empty] | Checked by: |  | A.G
Approved by:
Since,
For open type sprinklers dedicated for foam/water deluge systems,
Q (gpm) = K √P (psi)
And,
| K = | 3 | (Refer to ANSUL foam systems design and applications manual attached)
and since we have two approaches, one is to satisfy the density and the other is to satisfy
the minimum pressure required; we'll calculate both and apply the one with the greater demand.
i. Taking the design density as the governing constraint:
| Discharge Criteria = |  |  | 0.16 | gpm/ft2
| Q = | 10.8387 | gpm
| P = | 13.0531 | psi | (refused)
ii. Taking the minimum operating pressure as the governing constraint:
| P = | 30 | psi
| Q = | 16.4317 | gpm
| Discharge Criteria = |  |  | 0.24256 | gpm/ft2 | (accepted)
Therefore,
| Sp. No. | (gpm) | Pipe Diam.(in) | Eq. Pipe length (ft) |  | C | Pf (psi/ft) |  | Pt (psi)
| S1 | 16.4 | 0.5 | 8 |  | 120 | 3.3276 |  | 56.6208
| N1-N2 | 32.8 | 1 | 31 |  | 120 | 0.41022 |  | 69.3377
| N2-N3 | 65.6 | 1.5 | 20 |  | 120 | 0.20529 |  | 73.4434
| N3-N4 | 98.4 | 2 | 9 |  | 120 | 0.10707 |  | 74.407
| N4-System outlet | 98.4 | 2 | 15 |  | 120 | 0.10707 |  | 76.0131
Adding the static pressure:
|  |  |  | Pr = | 81 | psi
Design calculation sheet
Project no: | K0065 |  | Date: | 21/4/03 | Sheet no.: | 4 | 4 | Computed by: |  | A.R
Subject: | Foam Fire Extinguishing System Calculations | [6 empty] | Checked by: |  | A.G
Approved by:
Assuming that the induction causes a pressure drop of 30 % of the required pressure:
|  |  | Pt = | 106 | psi
Based on the final Design Criteria:
System Summary:
|  |  | Tank Capacity = |  | 31 | Gal.
|  |  | No. of Sprinklers = |  | 6 | Sprinklers
|  |  | Minimum Pressure Required at Input Point = |  |  |  |  | 106 | psi
of
of
of
of